## Page 1
Fire Door Corrective Actions Export Report
Barcode / Door Ref | Building | Level | Location | Location Description | Corrective Action No. | Defect / Description | Required Action | Impact | Probability | Status | Date Reported | Due Date
NWG0001 | Tudor House | First Floor | Board Room | Room C2 | NWG0001-001 | Hinge is broken | Repair or replace door or hinges | Major | High | New | 01/11/2023 | 01/02/2023
NWG0002 | Tudor House | First Floor | Data Room | Room 3S | NWG0002-001 | The door has a non-rated fire letter plate. | Letter plates must be suitable for use and detailed on the fire door certificate as a compatible component, and fitted in the correct location within the fire door leaf. | Medium | Medium | New | 07/09/2023 | 10/03/2023
NWG0003 | Tudor House | Second Floor | Assembly Room | Room B4 | NWG0003-001 | Intumescent and smoke seals are missing. | Seals fill the gap between the door and frame when the door is closed. Install intumescent seal or smoke seal. | Medium | Medium | New | 03/04/2023 | 10/04/2023
NWG0003 | Tudor House | Second Floor | Assembly Room | Room B4 | NWG0003-002 | Hinge is broken | Replace hinges immediately. | Major | Medium | New | 18/08/2023 | 24/09/2023
NWG0004 | Tudor House | First Floor | Battery Room | Block 27 | NWG0004-001 | Hinge is broken | Replace hinge. | Medium | High | New | 06/07/2023 | 06/10/2023
NWG0005 | Tudor House | First Floor | Boiler Room | Room F6 | NWG0005-001 | Refit the hinges to allow for the door to fit the frame. | Worn hinges causing door leaf to drop, resulting in incorrect gaps/problems with doorset operation. | Medium | Medium | New | 18/08/2023 | 2024-08-23
NWG0006 | Tudor House | First Floor | Service Riser | Block 4M | NWG0006-001 | Replace missing fixings. | Door latch bolt/keep plate or door bolt/socket misaligned preventing leaf from latching/closing. | Medium | High | New | 18/08/2023 | 2024-08-23
NWG0007 | Tudor House | First Floor | Stairway | Block 2J Stairway | NWG0007-001 | There are excessive gaps between the side of the door and the frame. | The gaps around the door should be less than 4mm once the door is shut. | Medium | High | New | 18/08/2023 | 2024-08-23